## Executive Summary & Register
AM/NS INDIA - PUNE FACILITY
GAS HAZARDOUS AREA MASTER SAFETY REGISTER & HAZARD CONTROL MATRIX
TOTAL GAS HAZARD AREAS |  | HIGH RISK AREAS |  | MEDIUM RISK AREAS
Area ID | Hazard Area Location | Primary Gas Species | Flammability | Toxicity / Asphyxiation | Hazard Zone Classification | Overall Risk Level
* Note: Complete technical details, gas detection systems, interlocks, PPE, and SOP references are detailed in the 'Hazard Assessment Matrix' tab.

## Hazard Assessment Matrix
AM/NS INDIA PUNE - COMPREHENSIVE GAS HAZARD & SAFETY CONTROL MATRIX
Mandatory Operational Safety Data Parameters for 16 Gas Hazardous Areas
AREA IDENTIFICATION |  | GAS HAZARD CHARACTERISTICS |  |  |  |  | ENGINEERING CONTROLS & MITIGATION |  |  |  | PROCEDURAL & PPE CONTROLS |  | RISK
Area ID | Hazard Area Location | Primary Gas Present | Flammable? (Yes/No) | Toxic / Asphyxiant? | Hazard Zone / Area Class | LEL / UEL / Exposure Limit | Potential Ignition Sources | Gas Detection System | Safety Interlocks & Trips | Ventilation Systems | Mandatory PPE Requirements | Applicable SOPs & Permits | Risk Level
HAZ-01 | NG Yard | Natural Gas (Methane CH4) | Yes | No (Asphyxiant) | Zone 1 / Zone 2 | 5.0% - 15.0% | Electrical sparks, static, hot work, vehicles, lightning | Fixed Gas Detectors (IR/Pellistor), Flame Detectors (UV/IR) | Auto Shut-Off Valve (Solenoid/ESD), Pressure Safety Valve (PSV) | Open-air Natural Ventilation, Explosion-proof forced air | Antistatic FR Clothing, Safety Helmet, Safety Shoes, Portable LEL Detector | SOP-NGY-001 (Gas Unloading), Permit to Work (Hot Work / CSE) | High
HAZ-02 | Propane Yard | Propane (C3H8) / LPG | Yes | No (Asphyxiant) | Zone 0 / Zone 1 | 2.1% - 9.5% | Static charge, open flame, electrical switches, friction sparks | Fixed Catalytic/IR Gas Detectors, Gas Cloud Detectors, Deluge Activation | Emergency Shut-Down Valve (ESDV), Excess Flow Check Valve | Low-level Natural/Forced Ventilation (Propane heavier than air) | Antistatic FR Suit, Cryogenic/Heat Gloves, Portable Multi-gas Monitor | SOP-PRP-002 (Bullet Tank Operations), Static Earthing Checklist | High
HAZ-03 | Ammonia Yard | Anhydrous Ammonia (NH3) | Yes (High energy required) | Yes (Highly Toxic/Corrosive) | Zone 2 (Toxic Primary) | 15.0% - 28.0% ¦ STEL: 35 ppm | High temp sources, static discharges, electrical arcs | Fixed Electrochemical NH3 Gas Detectors, Water Curtain System | Remote ESDV, Auto Water Spray Deluge on Leak Detection (>25 ppm) | Forced Exhaust Air Scrubbers, Open Canopy Ventilation | Chemical Suit (Level B/A), Ammonia Cartridge Respirator / SCBA | SOP-AMN-003 (Ammonia Storage & Transfer), Toxic Leak ERP | High
HAZ-04 | ARP Valve Stand | RCL Gas / Hydrogen Chloride Gas / Fuel Gas | Yes (Fuel component) | Yes (Corrosive & Toxic) | Zone 2 | Varies by Fuel ¦ HCl OEL: 2 ppm | Flange leaks onto hot surfaces, electrical equipment, maintenance tools | Fixed HCl & Combustible Gas Detectors | Pneumatic Quick-Closing Shut-off Valves, Line Pressure Switch Interlock | Local Exhaust Ventilation (LEV), Open Valve Station Canopy | Acid-resistant Suit, Face Shield, Acid Gas Respirator, Antistatic Boots | SOP-ARP-004 (Valve Stand Line Isolation), LOTO Procedure ARP-02 | Medium
HAZ-05 | CGL1 Valve Stand | NG / Mixed Fuel Gas / H2 Blend | Yes | Yes (CO presence in fuel gas) | Zone 1 / Zone 2 | 4.0% - 75.0% (Blend dependent) | Hot pipes, valve flange friction, electrical control panels | Fixed Gas Leak Detectors (Methane/H2/CO combo) | Dual Block & Bleed Valve Assembly, Low Line Pressure Trip | Mechanical Exhaust Ventilation in Enclosures | FR Coveralls, Portable Gas Monitor (CO/LEL), Leather Impact Gloves | SOP-CGL1-VS01 (Gas Skid Valve Operation), Flange Tightening Spec | High
HAZ-06 | CGL2 Valve Stand | NG / Mixed Fuel Gas / H2 Blend | Yes | Yes (CO presence in fuel gas) | Zone 1 / Zone 2 | 4.0% - 75.0% (Blend dependent) | Hot pipes, electrical switches, non-spark proof tools during maintenance | Fixed Gas Leak Detectors (Methane/H2/CO combo) | Dual Block & Bleed Valve System, Automatic Safety Shutoff | Forced Extraction Fans, Louvered Enclosure Wall | FR Coveralls, Portable 4-Gas Detector, Antistatic Safety Shoes | SOP-CGL2-VS01 (Gas Skid Main Valve Operation), LOTO Matrix | High
HAZ-07 | CGL1 Furnace | HNX Gas (H2/N2) / Natural Gas | Yes | Yes (CO byproduct / Nitrogen Asphyxiant) | Zone 1 (Inside/Surrounding) | 4.0% - 75.0% (H2 in HNX) | Furnace Burners, Radiant Tubes, Heat Exchangers, Electrical Heaters | Furnace Ambient H2/NG Detectors, Flame Scanners, O2 Analyzers | Furnace Purge Interlock (N2 Purge before ignition), Flame Failure Switch | Roof Extraction Canopy, Radiant Heat & Fume Exhaust Fans | Aluminized Heat Suit / FR Garment, Multi-gas Detector, SCBA for entry | SOP-CGL1-FRN01 (Furnace Light-up & Purging), Confined Space Permit | High
HAZ-08 | CGL2 Furnace | HNX Gas (H2/N2) / Natural Gas | Yes | Yes (CO byproduct / Nitrogen Asphyxiant) | Zone 1 (Inside/Surrounding) | 4.0% - 75.0% (H2 in HNX) | Furnace Burners, High Temp Rollers, Hot Strip, Electrical Igniters | Furnace Ambient H2/NG Detectors, Optical Flame Detectors, Combustible Monitors | N2 Auto Purge Interlock, Gas Safety Shutoff Valve (GSSV), Temp High Trip | High-capacity Roof Exhaust, Forced Draft Blowers | Aluminized Heat Resistant FR Clothing, Portable H2/CO Detector | SOP-CGL2-FRN01 (Furnace Start-up & HNX Purge), Hot Work Permit | High
HAZ-09 | PSA Plant | Hydrogen (H2) / Nitrogen (N2) | Yes (H2 Stream) | No (N2 Asphyxiant) | Zone 0 (Adsorber Vessel) / Zone 1 | 4.0% - 77.0% | Extremely low ignition energy required for H2; static, electrical panels | Fixed Ultrasonic Gas Leak Detectors, Catalytic H2 Sensors | Automatic Pressure Relief Valves, High Pressure Trip ESD | High Level Natural Ventilation (H2 rises rapidly), Explosive Proof Exhaust | Antistatic FR Suit, Static-Discharge Safety Shoes, Personal Gas Monitor | SOP-PSA-001 (PSA Bed Regeneration & Cycling), H2 Safety Guidelines | High
HAZ-10 | CCL1 RTO | Natural Gas / Solvent Vapors (VOCs) | Yes | Yes (VOCs & CO combustion gases) | Zone 2 | 1.1% - 7.0% (Solvent Vapors) / 5-15% (NG) | Combustion Chamber Open Flame, Ceramic Beds, Exhaust Duct Hot Spots | In-line LEL VOC Analyzers, NG Gas Leak Detectors, Flame Scanners | High LEL Exhaust Diverter Damper, Auto Burner Trip on Loss of Flame | Process Exhaust Fans, LEV Hoods over Coater Rooms | FR Clothing, Organic Vapor Respirator, Leather Safety Gloves | SOP-CCL1-RTO01 (RTO Preheat & Bypass Operations), VOC Monitoring | Medium
HAZ-11 | CCL2 RTO | Natural Gas / Solvent Vapors (VOCs) | Yes | Yes (VOCs & CO combustion gases) | Zone 2 | 1.1% - 7.0% (Solvent Vapors) / 5-15% (NG) | Combustion Chamber Flame, Ceramic Heat Exchanger, High Temp Exhaust | In-line Flame Ionization Detectors (FID) / LEL Sensors, UV Flame Sensors | Emergency Fresh Air Damper Interlock, Low Combustion Air Pressure Trip | RTO Main Draft Fans, Exhaust Duct Static Pressure Controllers | FR Clothing, Organic Vapor Mask, Protective Eyewear, Steel Toe Boots | SOP-CCL2-RTO01 (RTO Start/Stop Sequence), Coater Exhaust Safety | Medium
HAZ-12 | CCL1 Oven | Natural Gas / Solvent Exhaust Gas | Yes | Yes (Solvent fumes / Carbon Monoxide) | Zone 1 / Zone 2 | Varies by solvent composition (Typically 1-8%) | Direct/Indirect Gas Burners, Hot Oven Zone Walls, Conveyor Friction | Continuous Solvent LEL Analyzers in Oven Zones, Gas Pressure Switches | Oven Purge Time Delay Interlock (4 volume changes before ignition) | Recirculation Blowers, Fresh Air Make-up Fans, LEV Fume Extraction | Heat-Resistant Gloves, FR Apparel, Chemical/Vapor Respirators | SOP-CCL1-OVN01 (Curing Oven Startup), LEL Alarm Response SOP | High
HAZ-13 | CCL2 Oven | Natural Gas / Solvent Exhaust Gas | Yes | Yes (Solvent fumes / Carbon Monoxide) | Zone 1 / Zone 2 | Varies by solvent composition (Typically 1-8%) | Gas Burner Systems, Hot Air Nozzles, Heated Strip Surfaces | Zone-wise LEL Monitoring, Gas Header Leak Detection | Exhaust Air Flow Switch Interlock (Trips gas if airflow fails) | Oven Exhaust Blowers, Negative Pressure Duct Controllers | Heat/FR Protection Gear, Organic Vapor Face Respirator, Safety Glasses | SOP-CCL2-OVN01 (Catenary Oven Operation), Fume Hood Maintenance | High
HAZ-14 | CCL1 Valve Stand | Natural Gas / Fuel Gas | Yes | No (Primary Fuel) / Minor CO risk | Zone 2 | 5.0% - 15.0% | Electrical junction boxes, maintenance grinding, hot surfaces nearby | Fixed Methane Gas Sensors | Manual & Automated Emergency Isolation Valve (EIV), Pressure Regulators | Natural Cross-ventilation, Wall Exhaust Louvers | FR Coveralls, Portable Single-gas LEL Detector, Safety Shoes | SOP-CCL1-VS01 (Fuel Gas Skid Inspection), Valve Maintenance SOP | Medium
HAZ-15 | CCL2 Valve Stand | Natural Gas / Fuel Gas | Yes | No (Primary Fuel) / Minor CO risk | Zone 2 | 5.0% - 15.0% | Electrical switches, static charges, non-certified electronic devices | Fixed Methane Gas Sensors | Pneumatic Safety Shutoff Valve, High/Low Gas Pressure Switches | Natural Cross-ventilation, Open Air Skid Structure | FR Coveralls, Portable LEL Detector, Antistatic Gloves | SOP-CCL2-VS01 (Fuel Gas Skid Inspection), Line Bleeding SOP | Medium
HAZ-16 | Boiler House | Natural Gas / Flue Gas / CO | Yes | Yes (Carbon Monoxide in flue gas) | Zone 2 | 5.0% - 15.0% (NG) ¦ CO LEL: 12.5% - 74% | Boiler Main Burners, Pilot Flames, High Temp Steam Pipes, Electrical Controls | Fixed NG Gas Sensors, Ambient CO Detectors, Stack Gas Analyzers (O2/CO) | Boiler Master Fuel Trip (MFT), Pre-purge Interlock, Low Water Level Trip | Forced Draft (FD) Fans, Induced Draft (ID) Fans, High Ceiling Louvers | FR Clothing, Heat Gloves, Portable CO/LEL Dual Monitor, Ear Protection | SOP-BLR-001 (Boiler Light-up & Purging), Steam Boiler Operating Code | High

## Safety Reference Guide
GAS SAFETY REFERENCE MANUAL & PARAMETER GUIDE
Definitions, Mandatory Safety Field Explanations & Area Classification Standards
MANDATORY SAFETY PARAMETERS EXPLAINED
Parameter Name | Safety Category | Description & Operational Importance | Key Reference Standards
Primary Gas Present | Hazard ID | Identifies the chemical composition of gases present (e.g., Methane, Propane, H2, NH3, CO). | IS/IEC 60079-20-1
Flammability & LEL/UEL | Fire/Explosion | Defines Lower & Upper Explosive Limits. Gas-air mixtures within this range can ignite explosively. | NFPA 54 / IS 5572
Toxicity / Asphyxiation | Health Hazard | Specifies Short-Term Exposure Limits (STEL/TWA) or asphyxiation hazards (O2 displacement). | OSHA 1910.1000 / ACGIH
Hazard Zone Class | Area Class | Zone 0 (Continuous risk), Zone 1 (Likely in normal operation), Zone 2 (Unlikely/Short duration). | IS/IEC 60079-10-1
Ignition Sources | Prevention | Identifies potential heat, electrical, static, or mechanical spark sources requiring control. | NFPA 70 / IS 7000
Gas Detection System | Engineering Control | Fixed sensors (IR, Catalytic, Electrochemical) for early gas leak warning at LEL/PPM thresholds. | IS/IEC 60079-29-1
Safety Interlocks & Trips | Engineering Control | Automated shutoff valves (ESDV/GSSV), trip switches, and deluge systems to isolate hazards. | ISA 84 / IEC 61511 (SIL)
Ventilation Systems | Engineering Control | Forced extraction, LEV, or natural ventilation to dilute gas leaks below flammable thresholds. | NFPA 91 / ASHRAE
Mandatory PPE Requirements | Personal Protection | FR clothing, antistatic boots, SCBA, toxic gas cartridges, and portable multi-gas detectors. | OSHA 1910.132 / IS Standards
Applicable SOPs & Permits | Procedural Control | Standard Operating Procedures, LOTO forms, Hot Work Permits, and Confined Space Permits. | AM/NS Safety Management System
HAZARDOUS AREA ZONE CLASSIFICATIONS (IS/IEC 60079)
Zone Classification | Presence of Explosive Gas Atmosphere | Equipment Protection Level (EPL) | Typical Plant Application
Zone 0 | Continuous, long periods, or frequently present (>1000 hrs/yr) | Ga (Very High Protection) | Inside gas pipes, vessel interiors, storage tanks
Zone 1 | Likely to occur in normal operation occasionally (10-1000 hrs/yr) | Gb (High Protection) | Adjacent to valve glands, sample points, burner fronts
Zone 2 | Not likely in normal operation; if occurs, persists briefly (<10 hrs/yr) | Gc (Enhanced Protection) | Outer yard areas, well-ventilated valve stands, piping runs